	Serial Number
	Failure Condition 


	Monitored by
	Action Taken 

By
	Status of Implementation
	Comment 

	25
	Communication loss with CSC DCS for HV and LV control and monitoring
	Operator
	Operator >>USC_Accessible -  Access USC and monitor or turn off via local PC
>>USC_NOT_Accessible can operate blind for several hours utilizing DSS and Local protections.  Beyond that need method of remote shut down.  
	USC_Accessible -  Need to formulate procedures

USC_NOT_Accessible Need method of remote shut down.
	The LV could be turned OFF remotely by turning off the Twidoes remotely.  The HV can run blind for up to 12 hours.  After that needs some method for remote turn off.

	26.
	High Temperature 
	Hardware, DCS and DSS
	Racks protected by DCS and DSS.  Maratons/PFC’s have internal thermal protection.  Peripheral crate back planes have internal protection.  Peripheral crate boards will not rise to dangerous temperatures with loss of cooling.  
Chamber electronics will not rise to dangerous temperatures with loss of cooling.  
	Basics implemented – upgrades to DCS in progress
	Hardware protection is in place for all hardware.  Have and will be adding DCS interventions.

	..
	..
	
	
	
	


Norisko Report Recommendations:

Norisko Report Recommendations status table:

	Serial Number
	Description
	Non mandatory

Actions
	Mandatory Actions


	Action Taken 
	Status of Implementation
	Comment 

	1.
	LV and HV cables not separated
	Yes
	
	No change
	
	All HV and LV cables are shielded and insulated by plastic jackets

	2.3
	In rack S1A11 ALL PHVPS not labeled
	
	Yes
	Labels in place
	Done
	

	4.
	In rack S1A11 AC power distribution box  not labeled
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	5.
	In rack S1A12 AC power distribution box  not labeled
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	6.
	In rack S1A12 grounding jumper to rear door has been damaged 
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	7.
	In rack S1A13 AC power distribution box  not labeled
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	8
	In rack S1A12 grounding jumper to rear door has been damaged
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	9.
	In rack S1A13 grounding jumper to rear door has mechanical problem
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	10.
	In rack S1G10 AC power distribution box  not labeled
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	11.
	In rack S1G10 CAEN HV 2 Ethernet cables have mechanical problem
	
	Yes
	Mechanical problem solved
	Done
	

	12.
	In rack S1G10 grounding jumper to rear door has been damaged
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	13.14.
	In many UXC55 LV racks “Plexiglas” screens not installed
	
	Yes
	“Plexiglas” screens installed in all racks where it is necessary
	Done
	“Plexiglas” screens not installed in all racks where Maraton LVPS located under air turbine or under upper equipment

	15.
	In many UXC55 LV racks labels not visible
	
	Yes
	Labels are installed on both sides of all EMU racks
	Done
	

	16.17
	In rack S4F04 AC power connection 

EXD20/55 and power distribution box not labeled
	
	Yes
	Pending
	Pending
	Work will start this week (S. Dos Santos).

	18.
	In rack X2A41 exists cable mechanical problem
	
	Yes
	Mechanical problem fixed
	Done
	

	19
	In rack X4J41 DC splitter box cable shielding lead not connected
	
	Yes
	Connection

done
	Done
	

	20.
	In rack X2J42 final label not exists
	
	Yes
	Labeling done
	
	

	21
	In rack X2J31 back cables not connected
	
	Yes
	Cabling done
	Done
	

	22.
	In rack S1A11 8 PHVPS

MATSUSADA

has missing labels with main HV parameters.
	
	Yes
	Labeling done
	Done
	

	23.
	In rack S4F04 in all  36 OPFC PIC  (Permanent Insulation Controller) circuit not found
	Yes
	
	PIC  (Permanent Insulation Controller) circuit  exists on the level of CMS UPS and implemented in  AC distribution cabinets located in S1.2,4
	Done
	

	24.
	In rack S4F04

connection to PE not found
	
	Yes
	Connection to PE done
	Done
	


