# CSC Action Matrixes and Safe Operation States

This document presents the Action Matrixes and the Safe Operation States for the CSC Sub-detector for CMS.

Table 1 – The major sub-divisions of the CSC sub-detector of CMS.

The CSC Sub-detector falls into three mostly independent systems.  The first of the three is the racks in counting room S1.  These are standard CMS racks and house the CSC Track Finder, CSC-TF, the CSC-TTC signal distribution rack, and the three FED racks.  The second is the HV system which spans S1 and the Cavern, UXC.    The third is the detector Low Voltage that spans S4 and the Cavern.

This document will address each of these three in order.

# CSC Hardware in S1

Table 2 – Safe Operation States for the CSC Racks in S1

Each of the 6 CSC racks located in S1 are independent.  A loss of Water, Turbine, or Power to any single rack or group of racks only requires that single rack or group of racks be switched OFF.

Table 3 – Action Matrix for CSC S1 Racks

The CSC hardware in S1 is all mounted within standard CMS racks.  Therefore they have the standard DSS protections plus the CMS DCS rack protections.  The above table lists only the High Temperature protections which under CMS DCS rack protections can be set at different temperature thresholds.  Protections for other eventualities such as water leeks, smoke detection, loss of DCS communication, all follow the CMS standard.

# CSC HV and Gas Systems

Table 4 – the Safe States for the CSC HV and Gas Systems

CSC gas system is within the CMS gas system.  Therefore conditions within the system are not addressed in this document.  This document considers only whether the entire CSC gas system is ON and functioning in the correct manner.

The CSC HV is in two parts.  The HV for the 72 ME1/1 chambers on YE+1 and YE-1, and the HV for the remaining 396 chambers.  The ME1/1 HV is provided by a CAEN system with the control crates located in S1G10.  For this system the HV is generated in S1 and conveyed directly to the chambers in the cavern via HV Cables.  The HV for the remainder of the chambers is a custom system located in the S1A racks and within tower racks in the cavern.  The HV is generated in S1 and conveyed to several tower racks where it is actively fanned out for the individual channels within individual chambers.  The HV from these racks is conveyed to each chamber via HV cables.  The distribution hardware located within the cavern tower racks requires power from each distribution rack for its active control.  A loss of power to a tower rack will result in the HV being shut OFF at that point.

Table 5 – The Action Matrix for the CSC HV system.

This system is located in 3 racks in S1 row A, and 8 racks in the cavern.  These 8 racks are located 4 on each of the PLUS and MINUS end disks in the tower racks on levels X2 and X4.

# CSC LV System and Other CSC UXC Racks

Table 6 – Safe Operation States for the LV System

Table 7 – Action Matrix for the CSC LV System and other Cavern Racks

Water flow failure

Sensor on disk loop senses water pressure drop

Rack DCS is notified

Rack DCS notifies CSC DCS and waits x sec

CSC DCS turns off appropriate PCB’s

CSC DCS Waits 0.5 sec

CSC DCS Turns off appropriate Maratons

Rack DCS turns off rack power

Table 8 – Action Matrix for CSC LV System

The CSC LV system receives its power from the CMS LV UPS system in S4.  In rack S4F04 the UPS power is converted to 385V DC by the Wiener Maraton System PFC modules and conducted to Maraton Power Crates mounted in tower racks located with end cap disk towers on levels X2 and X4.  Each Maraton has 6 outputs which are sent in pairs of outputs to either two trigger sectors, TS, of 9 chambers plus a single peripheral crate, pcrate, or to 3 pcrates.

Note 1 - Because the LV power is supplied externally to both the Maraton racks and the pcrate racks, the DSS for these racks must have a special set up.  First the DSS for each Maraton rack must be set up to trip the twidoe in S4 that supplies the UPS power to the PFC-Maraton combination.  Second, since each pcrate rack receives external LV power in turn from the Maraton rack, the DSS in each pcrate rack must be set up to trip the twidoe which originates the LV power for the pcrate rack.

Table 9 – DSS dependencies for pcrate racks.

A DSS alarm condition in any of the pcrate racks listed in the right columns, must result in DSS tripping the circuit breaker in the first column.  The DCS system must follow this same map for action taken.