## Modules
Number | Vendor | Discription |  | Location | rack | Input | Heat load | Controls
[8 empty] | DCS | local | external interlock | Internal Interlock
2 | Maraton | PFC | 0PFC.0000 | GB | xxx | 230V AC single phase |  | no | switch on front pannel | AC from rack interlocked | yes *
1 | Maraton | Dist Box | 0M14.0003 | Tower | X2J31 | 380V DC |  | yes |  | no external | yes *
1 | Maraton | Dist Box | 0M14.0003 | Tower | X2J41 | 380V DC |  | yes |  |  | yes *
1 |  | Patch Pannel | P/P 1 | GB | XX | 380V DC | 0 | no | no | no | no
1 |  |  | P/P 2 | Tower | X2J31 | 380V DC | 0 | no | no | no | no
1 |  |  | P/P 3 | Tower | X2J41 | 380V DC | 0 | no | no | no | no
•List of circuits (power supplies, ratings)
cable cross sections, types and lengths,
protection (i.e. fusing or other),
identification of cables,
ways to cut the circuits in case of emergency,
cooling interlocks if applicable,
unifilar schematics,
earthing
•any other hazard specific to subsystem / sub det
* See Vendor Information

## Maraton details
Number |  | MARATON |  | Inst. | Ordering No.: | Ex-Works Prices for |  | Ex-Works Prices for
for |  | fully halogenfree technology |  | In |  | Series | Repair | Series | Repair
MTCC | Item | Power Supply, Power Bin, Prim. PFC and Control |  | Environ |  | EURO | EURO | EURO | EURO
|  | LV-P.- Supplies, all with min. 110% current limit | No. Of | ment | Air cooled
|  | 3U modular power boxes, | Ch. |  | 0M1x.xxxx
2 | A1a | 2-8V/50A- 300W 8V peak ext p+m | 12 | 4 | 0M14.0003 | 6216 | 1250 | 12432 | 2500
|  | 6U and 3U Power Bins for MARATON Power Supplies, controlled output impedance (>50/200R@0,5/5MHz) | [6 empty] | 0
|  | Environment 4 | [6 empty] | 0
2 |  | Power Bin MARI 3U 6 channels 600W | 6 | 4 | 0B23.0600 | 1146.5 | 210 | 2293 | 420
2 |  | Primary Rectifier Module PFC | 4-24 | SE | 0PFC.0000 | 1095 | 245 | 2190 | 490
1 |  | Primary Rectifier Power Bin for PFC, 6 slot | 24-72 | SE | 0B07.0000 | 590 | 150 | 590 | 150
0
1 |  | Control Crate, NIXI-C, VME 6U +1U fan unit | 252 | SE | 0300.M921 | 1515 | 250 | 1515 | 250
0
0 |  | Control and Monitoring Module RCM, 6U VME | 12 | SE | 0R00.0000 | 725 | 175 | 0 | 0
|  | TCP/IP Software for RCM with OPC Server, | [5 empty] | 0 | 0
0 |  | Single Unit / per user | 12 | SE | 0S00.0001 | 170 | 31 | 0 | 0
[8 empty] | 19020 | 3810

## LV Cables ACtoWM
Cable
| From | To | Use | length | type | wires | voltage | amps | watts | earth | GND wire | shield | cross section
| GB breaker | PFC 1 | AC power | 2 |  | +/- | 230 | 0 | 0 | 1
[6 empty] | earth | 0
| PFC 1 | WM PP 1 | DC power | 2 |  | S/R | 380 | 0 | 0 |  | 1
ground
| GB breaker | PFC 1 | AC power | 2 |  | +/- | 230 | 0 | 0 | 1
[6 empty] | earth | 0
| PFC 1 | WM PP 1 | DC power | 2 |  | S/R | 380 | 0 | 0 |  | 1
ground
| WM PP 1 | WM PP 2 | DC power | 140 | 7x6mm2 | S/R 1 | 380 | 0 | 0 |  | 1 |  | 6
[6 empty] | S/R 2 | 380 | [5 empty] | 6
[6 empty] | ground | [6 empty] | 6
shield
| WM PP 2 | WM PP 3 | DC power | 40 | 7x8mm2 | S/R 1 | 380 | 0 | 0 |  | 1 |  | 6
[6 empty] | S/R 2 | 380 | [5 empty] | 6
[6 empty] | ground | [6 empty] | 6
shield
| WM PP 3 | WM PP 4 |  | 2 | 4x6mm2 | S/R | 380 | [5 empty] | 6
[6 empty] | ground | [6 empty] | 6
shield
| WM PP 3 | WM 1 |  | 2 |  | S/R | 380
ground
| WM PP 4 | WM 2 |  | 2 |  | S/R | 380
ground
•List of circuits (power supplies, ratings)
cable cross sections, types and lengths,
protection (i.e. fusing or other),
identification of cables,
ways to cut the circuits in case of emergency,
cooling interlocks if applicable,
unifilar schematics,
earthing

## LV Cables WMtoLoad
Cable
| From | To | Use | length | wires | voltage | amps | watts | earth | GND wire | shield | cross section
| WM 1 | VME+1/9 | DC power | 9 | 4.5V S/R | 7 | 0 | 0 |  | 1 |  | 12 |  | •any other hazard specific to subsystem / sub det
[5 empty] | 6.5V S/R | 7 | 0 | 0 |  | 1 |  | 12
[5 empty] | shield | 0 |  |  |  | 1
| WM 1 | LVJB ME+1/9 | DC power | 2 | Digital LV | 8 | 140 | 1120 |  |  |  | 32
[5 empty] | Analog LV | 8 | 80 | 640 |  |  |  | 16
| LVJB ME+1/9 | CSC ME+1/1/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/1/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/1/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  | 1 |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  | 1 |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| WM 1 | VME+1/10 | DC power | 9 | 4.5V S/R | 7 | 0 | 0 |  | 1 |  | 12
[5 empty] | 6.5V S/R | 7 | 0 | 0 |  | 1 |  | 12
[5 empty] | shield | 0 |  |  |  | 1
| WM 1 | LVJB ME+1/10 | DC power | 2 | Digital LV | 8 | 140 | 1120 |  |  |  | 32
[5 empty] | Analog LV | 8 | 80 | 640 |  |  |  | 16
| LVJB ME+1/9 | CSC ME+1/1/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/1/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/1/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  | 1 |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  | 1 |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| WM 2 | VME+2/5 | DC power | 9 | 4.5V S/R | 7 | 0 | 0 |  | 1 |  | 12
[5 empty] | 6.5V S/R | 7 | 0 | 0 |  | 1 |  | 12
[5 empty] | shield | 0 |  |  |  | 1
| WM 2 | LVJB ME+1/9 | DC power | 2 | Digital LV | 8 | 140 | 1120 |  |  |  | 32
[5 empty] | Analog LV | 8 | 80 | 640 |  |  |  | 16
| LVJB ME+1/9 | CSC ME+1/1/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/1/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/1/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  | 1 |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  | 1 |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| WM 1 | VME+3/5 | DC power | 9 | 4.5V S/R | 7 | 0 | 0 |  | 1 |  | 12
[5 empty] | 6.5V S/R | 7 | 0 | 0 |  | 1 |  | 12
[5 empty] | shield | 0 |  |  |  | 1
| WM 1 | LVJB ME+1/10 | DC power | 2 | Digital LV | 8 | 140 | 1120 |  |  |  | 32
[5 empty] | Analog LV | 8 | 80 | 640 |  |  |  | 16
| LVJB ME+1/9 | CSC ME+1/1/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/1/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/1/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  | 1 |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  | 1 |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/2/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/17 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/18 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a
| LVJB ME+1/9 | CSC ME+1/3/19 |  | 11 | D LV | 8 | 15.5556 | 124.4444 |  |  |  |  | supply fused in LVJB -10a
[5 empty] | A LV | 8 | 8.8889 | 71.1111 |  |  |  |  | supply fused in LVJB -10a