## EXFO_YE1_3SM_2007-05-07_15-09
FasTesT Results TUBE 3 PP(YE1)
Fiber Id | Wavelength (nm) | Loss A (dB) | Loss A Reference (dB) | Loss B (dB) | Loss B Reference (dB) | Average Loss (dB) | ORL A (dB) | Sensitivity ORL A (dB) | ORL A Reference (%) | ORL B (dB) | Sensitivity ORL B (dB) | ORL B Reference (%) | Length (km) | Comment | Wavelength A (m) | Wavelength B (m) | Temperature A (Celsius) | Temperature B (Celsius) | Date | Time | Fiber Type | Reference Type | Reference | type | module | channel
FIBER001 | 1310 | 0.2849 | 0.30454 | 0.28755 | 0.21915 | 0.28622 | 100 | 44.265 | 0 | 100 | 44.4337 | 0 | 0.0818 |  | 1.3036e-06 | 1.3156e-06 | 24.4375 | 24.7812 | 2007-05-07 | 15:10 | 9/125 microns SM | Side by Side | X3A31 | CCB | 8 | 1
| 1550 | 0.18444 | 0.12519 | 0.20622 | 0.12738 | 0.19531 | 100 | 44.9717 | 0 | 100 | 45.1122 | 0 | 0.0818 |  | 1.5543e-06 | 1.5462e-06 | 24.4375 | 24.7812 | 2007-05-07 | 15:10 | 9/125 microns SM | Side by Side | X3A31
FIBER002 | 1310 | 0.22907 | 0.30454 | 0.21982 | 0.21915 | 0.22444 | 100 | 44.1616 | 0 | 100 | 44.3081 | 0 | 0.0816 |  | 1.3036e-06 | 1.3156e-06 | 24.4844 | 24.7812 | 2007-05-07 | 15:10 | 9/125 microns SM | Side by Side | X3A31 | CCB | 8 | 2
| 1550 | 0.36593 | 0.12519 | 0.29501 | 0.12738 | 0.33032 | 100 | 45.3056 | 0 | 100 | 45.2764 | 0 | 0.0816 |  | 1.5543e-06 | 1.5462e-06 | 24.4844 | 24.7812 | 2007-05-07 | 15:10 | 9/125 microns SM | Side by Side | X3A31
FIBER003 | 1310 | 0.48799 | 0.30454 | 0.38057 | 0.21915 | 0.43395 | 100 | 44.6395 | 0 | 100 | 44.6056 | 0 | 0.082 |  | 1.3036e-06 | 1.3157e-06 | 24.5 | 24.8125 | 2007-05-07 | 15:11 | 9/125 microns SM | Side by Side | X3A31 | CCB | 8 | 3
| 1550 | 0.35803 | 0.12519 | 0.33861 | 0.12738 | 0.34831 | 100 | 45.2911 | 0 | 100 | 45.3569 | 0 | 0.082 |  | 1.5544e-06 | 1.5462e-06 | 24.5 | 24.8125 | 2007-05-07 | 15:11 | 9/125 microns SM | Side by Side | X3A31
FIBER004 | 1310 | 0.76265 | 0.30454 | 0.78378 | 0.21915 | 0.7732 | 53.6565 | 45.1412 | 0 | 100 | 45.3439 | 0 | 0.0819 |  | 1.3036e-06 | 1.3157e-06 | 24.5469 | 24.8281 | 2007-05-07 | 15:11 | 9/125 microns SM | Side by Side | X3A31 | CCB | 8 | 4
| 1550 | 0.54937 | 0.12519 | 0.55929 | 0.12738 | 0.55433 | 100 | 45.6407 | 0 | 100 | 45.7622 | 0 | 0.0819 |  | 1.5544e-06 | 1.5462e-06 | 24.5469 | 24.8281 | 2007-05-07 | 15:11 | 9/125 microns SM | Side by Side | X3A31
Threshold
Name:
Wavelength (nm) | Insertion Loss (dB) | ORL (dB) | Power (dBm) | Power Ref. (dB)
Cable Information
Id: | YE1_3SM
Manufacturer:
Type:
Comment:
Location A:
Location B:
Job Information
Id:
Contractor:
Customer:
Reason:
Operator A:
Unit A: | FOT-930
Serial Number A: | 397285
Operator B:
Unit B: | FOT-932
Serial Number B: | 397286
Date: | 2007-05-07 | 15:10