## EXFO_YE1_5SM_2007-05-07_15-14
FasTesT Results TUBE 5 PP(YE1)
Fiber Id | Wavelength (nm) | Loss A (dB) | Loss A Reference (dB) | Loss B (dB) | Loss B Reference (dB) | Average Loss (dB) | ORL A (dB) | Sensitivity ORL A (dB) | ORL A Reference (%) | ORL B (dB) | Sensitivity ORL B (dB) | ORL B Reference (%) | Length (km) | Comment | Wavelength A (m) | Wavelength B (m) | Temperature A (Celsius) | Temperature B (Celsius) | Date | Time | Fiber Type | Reference Type | Reference | type | module | channel
FIBER001 | 1310 | 0.50742 | 0.30454 | 0.58404 | 0.21915 | 0.54556 | 28.1884 | 44.6751 | 0 | 27.3084 | 44.9796 | 0 | 0.0599 |  | 1.3036e-06 | 1.3157e-06 | 24.5312 | 24.7969 | 2007-05-07 | 15:16 | 9/125 microns SM | Side by Side | X1U31 | CCB | 8 | 1
| 1550 | 0.43947 | 0.12519 | 0.50056 | 0.12738 | 0.46991 | 28.6368 | 45.4402 | 0 | 27.9105 | 45.6547 | 0 | 0.0599 |  | 1.5544e-06 | 1.5462e-06 | 24.5312 | 24.7969 | 2007-05-07 | 15:16 | 9/125 microns SM | Side by Side | X1U31
FIBER002 | 1310 | 0.20675 | 0.30454 | 0.10253 | 0.21915 | 0.15433 | 35.3016 | 44.1203 | 0 | 35.1258 | 44.0901 | 0 | 0.0604 |  | 1.3036e-06 | 1.3157e-06 | 24.5625 | 24.8281 | 2007-05-07 | 15:16 | 9/125 microns SM | Side by Side | X1U31 | CCB | 8 | 2
| 1550 | 0.2524 | 0.12519 | 0.14647 | 0.12738 | 0.19912 | 36.3197 | 45.097 | 0 | 36.211 | 45.0014 | 0 | 0.0604 |  | 1.5544e-06 | 1.5462e-06 | 24.5625 | 24.8281 | 2007-05-07 | 15:16 | 9/125 microns SM | Side by Side | X1U31
FIBER003 | 1310 | 0.40842 | 0.30454 | 0.48133 | 0.21915 | 0.44472 | 37.0337 | 44.4931 | 0 | 36.0319 | 44.7912 | 0 | 0.0604 |  | 1.3036e-06 | 1.3157e-06 | 24.5938 | 24.8281 | 2007-05-07 | 15:17 | 9/125 microns SM | Side by Side | X1U31 | CCB | 8 | 3
| 1550 | 0.40283 | 0.12519 | 0.40203 | 0.12738 | 0.40243 | 37.991 | 45.3732 | 0 | 37.1715 | 45.4738 | 0 | 0.0604 |  | 1.5544e-06 | 1.5462e-06 | 24.5938 | 24.8281 | 2007-05-07 | 15:17 | 9/125 microns SM | Side by Side | X1U31
FIBER004 | 1310 | 0.27624 | 0.30454 | 0.24463 | 0.21915 | 0.26041 | 41.4092 | 44.249 | 0 | 40.9551 | 44.3542 | 0 | 0.0604 |  | 1.3036e-06 | 1.3157e-06 | 24.5781 | 24.8281 | 2007-05-07 | 15:17 | 9/125 microns SM | Side by Side | X1U31 | CCB | 8 | 4
| 1550 | 0.19229 | 0.12519 | 0.21738 | 0.12738 | 0.20482 | 42.4391 | 44.9862 | 0 | 42.2274 | 45.1329 | 0 | 0.0604 |  | 1.5544e-06 | 1.5462e-06 | 24.5781 | 24.8281 | 2007-05-07 | 15:17 | 9/125 microns SM | Side by Side | X1U31
Threshold
Name:
Wavelength (nm) | Insertion Loss (dB) | ORL (dB) | Power (dBm) | Power Ref. (dB)
Cable Information
Id: | YE1_5SM
Manufacturer:
Type:
Comment:
Location A:
Location B:
Job Information
Id:
Contractor:
Customer:
Reason:
Operator A:
Unit A: | FOT-930
Serial Number A: | 397285
Operator B:
Unit B: | FOT-932
Serial Number B: | 397286
Date: | 2007-05-07 | 15:14