## EXFO_YE1_6SM_2007-05-07_15-18
FasTesT Results TUBE 6 PP(YE1)
Fiber Id | Wavelength (nm) | Loss A (dB) | Loss A Reference (dB) | Loss B (dB) | Loss B Reference (dB) | Average Loss (dB) | ORL A (dB) | Sensitivity ORL A (dB) | ORL A Reference (%) | ORL B (dB) | Sensitivity ORL B (dB) | ORL B Reference (%) | Length (km) | Comment | Wavelength A (m) | Wavelength B (m) | Temperature A (Celsius) | Temperature B (Celsius) | Date | Time | Fiber Type | Reference Type | Reference
FIBER001 | 1310 | 0.96202 | 0.30454 | 0.87686 | 0.21915 | 0.91923 | 41.1214 | 45.5019 | 0 | 40.4164 | 45.5127 | 0 | 0.0696 |  | 1.3036e-06 | 1.3157e-06 | 24.5781 | 24.8125 | 2007-05-07 | 15:19 | 9/125 microns | Side by Side | X3J31
| 1550 | 0.69642 | 0.12519 | 0.68995 | 0.12738 | 0.69319 | 41.8362 | 45.9075 | 0 | 41.6178 | 46.0006 | 0 | 0.0696 |  | 1.5544e-06 | 1.5462e-06 | 24.5781 | 24.8125 | 2007-05-07 | 15:19 | 9/125 microns | Side by Side | X3J31
FIBER002 | 1310 | 0.68879 | 0.30454 | 0.69955 | 0.21915 | 0.69417 | 41.3833 | 45.0069 | 0 | 41.4358 | 45.1907 | 0 | 0.0694 |  | 1.3036e-06 | 1.3157e-06 | 24.5781 | 24.8281 | 2007-05-07 | 15:19 | 9/125 microns | Side by Side | X3J31
| 1550 | 0.52614 | 0.12519 | 0.53894 | 0.12738 | 0.53254 | 42.573 | 45.5984 | 0 | 42.6857 | 45.725 | 0 | 0.0694 |  | 1.5544e-06 | 1.5462e-06 | 24.5781 | 24.8281 | 2007-05-07 | 15:19 | 9/125 microns | Side by Side | X3J31
FIBER003 | 1310 | 0.92084 | 0.30454 | 1.3623 | 0.21915 | 1.136 | 43.5465 | 45.4277 | 0 | 40.509 | 46.381 | 0 | 0.0691 |  | 1.3036e-06 | 1.3157e-06 | 24.625 | 24.8438 | 2007-05-07 | 15:19 | 9/125 microns | Side by Side | X3J31
| 1550 | 0.70917 | 0.12519 | 1.0515 | 0.12738 | 0.87696 | 44.8763 | 45.9305 | 0 | 41.8225 | 46.6532 | 0 | 0.0691 |  | 1.5544e-06 | 1.5463e-06 | 24.625 | 24.8438 | 2007-05-07 | 15:19 | 9/125 microns | Side by Side | X3J31
FIBER004 | 1310 | 0.51357 | 0.30454 | 0.47163 | 0.21915 | 0.49255 | 100 | 44.6864 | 0 | 100 | 44.7733 | 0 | 0.0699 |  | 1.3036e-06 | 1.3157e-06 | 24.625 | 24.875 | 2007-05-07 | 15:20 | 9/125 microns | Side by Side | X3J31
| 1550 | 0.34529 | 0.12519 | 0.359 | 0.12738 | 0.35214 | 100 | 45.2677 | 0 | 100 | 45.3945 | 0 | 0.0699 |  | 1.5544e-06 | 1.5463e-06 | 24.625 | 24.875 | 2007-05-07 | 15:20 | 9/125 microns | Side by Side | X3J31
Threshold
Name:
Wavelength (nm) | Insertion Loss (dB) | ORL (dB) | Power (dBm) | Power Ref. (dB)
Cable Information
Id: | YE1_6SM
Manufacturer:
Type:
Comment:
Location A:
Location B:
Job Information
Id:
Contractor:
Customer:
Reason:
Operator A:
Unit A: | FOT-930
Serial Number A: | 397285
Operator B:
Unit B: | FOT-932
Serial Number B: | 397286
Date: | 2007-05-07 | 15:18